## BOQ-Labour
Construction/Up-gradation of 220/110kV MCMV line
| Name of work: |  | Name of Packages:
| KLSP Project A& KLSP Project B |  | Kolathunadu Line strengthening Package- Up-grading 110kV SC line to 220/110kV MCMV line from Kanhirode to Mylatty line on Turnkey Basis (KLSP Project A and KLSP Project B)
| NMLP-A |  | Malabar Lines Package- PHASE 1A: Up-grading of 110kV SC & 66kV SC line from Mundayad to Thalassery to 220/110kV MCMV line on Turnkey Basis (NMLP Project A)
| NMLP-B |  | North Malabar Lines Package Phase 1B:- Construction/Upgradation of 220/110 KV MCMV line from Areekode- Kaniyambetta LILO point (near Malayamma) to Kunnamangalam S/S through Agasthiyamuzhi 110 kV DC line route on Turnkey Basis (NMLP Project B)
SL. NO. | ITEM DESCRIPTION | BILL OF QUANTITIES - LABOUR
|  | UNIT | Kolathunadu Package | North Malabar |  |  | Total Qty - KLSP+NMLP
|  |  | (KLSP Project A and KLSP Project B) | Project A | Project B | Total Qty
1 | 2 | 3 | 4 | 5 | 6 | 7=5+6 | 8=7+4
1 | Stub /probe setting
1.1 | Stub/probe setting of 400/220kV, 220/220kV, 220/110kV and 110/110kV towers as per approved schedule including surveying for marking and pegging of tower locations at site, stub setting in correct alignment using template/probe of all types of towers in concrete foundation / rock foundation excluding excavation, concreting and back filling but including grouting, anchoring, removing the template after completion etc. Complete in all respects as per scope and specification of work. | each | 292 | 98 | 0 | 98 | 390
1.2 | Stub/prop setting of 220/110kV and 110/110kV towers as per approved schedule including surveying for marking and pegging of tower locations at site, stub setting in correct alignment using template/prop of all types of towers in concrete foundation / rock foundation excluding excavation, concreting and back filling but including grouting, anchoring, removing the template after completion etc. Complete in all respects as per scope and specification of work. | each | 0 | 0 | 29 | 29 | 29
2 | Excavation of earth pit of size 0.3 x 0.3 x 3.6 m (Two Earthing per Location) including over excavation on account of sloping the banks and necessary hire for planks for filling of charcoal, earthing of tower by means of a 50 mm dia, 3 m long pipe and a double run 7/9 S.W.G galvanised steel wire or G.1 tape including cost of charcoal but excluding cost of pipes, steel wire or copper tape with connecting lugs, nuts, etc. including measurement of tower foot resistance by standard eqpt, Complete in all respects as per scope & specification of work | each | 584 | 200 | 58 | 258 | 842
3 | Counter poise earthing excavation for trench for burying the conductor 450mm below ground level, laying and connecting the conductor on to the tower legs, back filling and consolidating the soil after laying the conductor etc. Complete in all respects as per scope & specification of work | m | 1200 | 1500 | 200 | 1700 | 2900
4 | Erection of super structure above ground level, including erection of normal and special hill side extension members, where ever necessary, providing tower accessories like phase, danger and number plates, bird guards, anti climbing devices, circuit plates etc. complete in all respects as per scope & specification for following:
4.1 | 400/220kV& 220/110kV MultiCircuit Multi Voltage, 220/220kV &110/110kV MC Lattice Type Hot Dip Galvanized Steel Towers and Stub & cleat of various types (MLD for 400/220kV, KLA/B/C/D for 220/110kV, MD for 220/220kV & M3,M60 for 110/110kV ) complete with all tower parts & Extensions, Templates, including fastners, bolts & nuts,anti theft bolts and nuts along with spring washers , step bolts, hangers, D-shackles, pack washers, Danger plate, Circuit Plates,Number plate, Phase plate, Anti Climbing Device, Bird Guard, etc.complete in all respect as per scope & Technical specifications | MT | 6100 | 0 | 0 | 0 | 6100
4.2 | 400/220kV& 220/110kV Multi Circuit Multi Voltage & 220/220kV MC Lattice Type Hot Dip Galvanized Steel Towers and Stub & cleat of various types (MLD& MLS for 400/220kV, KLA/B/C/D for 220/110kV, MA & MB for 220/220kV ) complete with all tower parts & Extensions, Templates, including fastners, bolts & nuts,anti theft bolts and nuts along with spring washers , step bolts, hangers, D-shackles, pack washers, Danger plate, Circuit Plates, Number plate, Phase plate, Anti climbing device, Bird Guard, etc.complete in all respect as per scope & Technical specifications | MT | 0 | 2222 | 0 | 2222 | 2222
4.3 | 220/110kV MultiCircuit Multi Voltage, Lattice Type Hot Dip Galvanized Steel Towers and Stub & cleat of various types ( KLA/B/C/D ) complete with all tower parts & Extensions, Templates, including fastners, bolts & nuts,anti theft bolts and nuts along with spring washers , step bolts, hangers, D-shackles, pack washers, Danger plate,Circuit Plates, Number plate, Phase plate, Anti climbing device, Bird Guard, etc.complete in all respect as per scope & Technical specifications | MT | 0 | 0 | 736 | 736 | 736
5 | Stringing of conductors using Tension Puller Machine including attaching Polymer V type Suspension insulator strings with arcing horns or rings on to the cross arms, clamping conductor to the insulator strings using suspension clamps with armour rods, tension clamps, jumpering at tension points with pilot suspension insulators, wherever necessary, jointing of conductor and pilot wire, wherever necessary, installation of vibration dampers, including dismantling of 33kV or LT lines & re-stringing whereever required,hire charges of tractor and stringing tools,all hire and labour charges for protective devices,providing back stays etc. , complete in all respects as per scope & specification of work for the following:
5.1 | Six line Single/ Double ACSR Panther conductor for 110 kV/220kV Multi circuit | Km | 78 | 8 | 8 | 16 | 94
5.2 | Six line Double ACSR Panther conductor for 220kV Multi circuit | Km | 7.65 | 14.24 | 0 | 14.24 | 21.89
| Six line Single ACSR Panther conductor for 110 kV Double circuit | Km | 0 | 0 | 0 | 0 | 0
| Six line ACSR Kundah conductors for 220 KV Multicircuit | km | 3 | 0 | 0 | 0 | 3
| Six line ACSR Zebra conductor for 220kV Multi circuit | Km | 0 | 0 | 0 | 0 | 0
| Six line ACSR Quad-Moose conductor for 400kV Multi circuit | km | 0 | 0 | 0 | 0 | 0
| 12 line 'ACSR Kundah'' conductors | km | 0 | 0 | 0 | 0 | 0
| Stringing of one no. 7/9 SWG stranded steel GI earth wire | km | 0 | 0 | 0 | 0 | 0
6 | Tension stringing using tension puller machine as per standard of the follwing:
6.1 | 24/48 pair Optical Ground Wire (OPGW ASLH-D(S)b 48 SMF) including fixing of hardware accessories, fittings including cable fittings and accessories, etc, Pre-installation test (Drum Test), Post installation tests, Splicing and link test (End to End Test) and providing suitable back stays at the time of stringing,including the works involved in crossing LT/11kV/33kV lines viz dismantling and re-stringing,etc. complete in all respects as per scope & specification of work | km | 90 | 0 | 0 | 0 | 90
6.2 | 24/48 pair Optical Ground Wire (OPGW ASLH-D(S)b 24 SMF) including fixing of hardware accessories, fittings including cable fittings and accessories, etc, Pre-installation test (Drum Test), Post installation tests, Splicing and link test (End to End Test) and providing suitable back stays at the time of stringing,including the works involved in crossing LT/11kV/33kV lines viz dismantling and re-stringing,etc. complete in all respects as per scope & specification of work | km | 0 | 22.3 | 8 | 30.3 | 30.3
7 | Dismantling of conductors including detaching insulator strings with arcing horns or rings from the tower cross arms, disconnecting the jumpering at tension points, detaching of vibration dampers, hire charges of tractor and stringing tools, all hire and labour for protective trestle work, providing suitable back stays at the time of dismantling, etc. including the works involved in crossing LT/11kV/33kV lines viz dismantling and re-stringing, complete in all respects as per scope & technical specifications of following types:
7.1 | 3 line ACSR Kundah Conductor | km | 3 | 0 | 0 | 0 | 3
7.2 | 6 Line ACSR Wolf/Tiger/AAAC 150 sqmm conductor | km | 0 | 0 | 8 | 8 | 8
7.3 | 6 Line ACSR Wolf/Tiger/AAAC 120 sqmm conductor | km | 0 | 2.72 | 0 | 2.72 | 2.72
7.4 | 3 line ACSR Wolf/Tiger Conductor | km | 78 | 0 | 0 | 0 | 78
7.5 | 3 Line ACSR Wolf/Tiger/AAAC 120 sqmm conductor | km | 0 | 19.947 | 0 | 19.947 | 19.947
| 6 line ACSR DOG / Copper conductors | km | 0 | 0 | 0 | 0 | 0
| 3 line ACSR DOG / copper conductors | Km | 0 | 0 | 0 | 0 | 0
| 6 line ACSR WOLF/Tiger conductors | Km | 0 | 0 | 0 | 0 | 0
| 6 line ACSR Kundah conductors | Km | 0 | 0 | 0 | 0 | 0
| Dismantling as per standard of ACSR Quad-Moose conductors | km | 0 | 0 | 0 | 0 | 0
| 24/48 pair Optical Ground Wire (OPGW ASLH-D(S)b 24 SMF) including hardware, cable fittings and accessories, etc. | km | 0 | 0 | 0 | 0 | 0
8 | Dismantling of the following:
8.1 | Dismantling one no. 7/9/10 or 7/3.66/3.15 mm stranded steel earth wire from the existing 220kV MC / 110kV SC /66kV DC towers including detaching the tension clamps and suspension clamps, jumpers at tension points, earth bonds, hire charges of tractor and stringing tools, all hire and labour for protective trestles and providing suitable back stays complete in all respects as per scope & technical specifications. | km | 90 | 0 | 0 | 0 | 90
8.2 | Dismantling one no. 7/9/10 or 7/3.66/3.15 mm stranded steel earth wire from the existing 220kV DC / 110kV DC /66kV DC/SC towers including detaching the tension clamps and suspension clamps, jumpers at tension points, earth bonds, hire charges of tractor and stringing tools, all hire and labour for protective trestles and providing suitable back stays complete in all respects as per scope & technical specifications. | km | 0 | 22.3 | 0 | 22.3 | 22.3
8.3 | Dismantling one no. 7/9/10 or 7/3.66/3.15 mm stranded steel earth wire from the existing 220kV SC/DC- 110kV DC towers including detaching the tension clamps and suspension clamps, jumpers at tension points, earth bonds, hire charges of tractor and stringing tools, all hire and labour for protective trestles and providing suitable back stays complete in all respects as per scope & technical specifications. | km | 0 | 0 | 8 | 8 | 8
9 | Dismantling of tower superstructure above ground level including dismantling of tower accessories like phase, danger and number plates, bird guards, anticlimbing devices,circuit plates etc | MT | 1650 | 370 | 155 | 525 | 2175
10 | Clearing grass and removal of the rubbish upto a distance of 50m outside the periphery of the area cleared less than 1m. Complete in all respects as per scope & specification of work & technical specifications. | sqm |  |  |  | 0 | 0
Height of more than 1m above ground level
Less than 1m above ground level
11 | Felling trees of girth(measured at aheight of 1m above ground level) including cutting of trunks and branchs removing the roots and stacking of serviceable material and disposal of unserviceable material. Complete in all respects as per scope & specification of work & technical specifications.
11.1 | Beyond 30cm girth upto and including 60cm girth | Each | 1800 | 460 | 160 | 620 | 2420
11.2 | Beyond 60cm girth upto and including 120cm girth | Each | 1350 | 345 | 120 | 465 | 1815
11.3 | Beyond 120cm girth upto and including 240cm girth | Each | 900 | 230 | 80 | 310 | 1210
11.4 | Above 240cm girth | Each | 450 | 115 | 40 | 155 | 605
12 | Detailed Survey of the route along the alignment fixed by KSEBL, preparation of the longitudinal profiles of the route showing all site details of the terrain for the full corridor of the line route, plotting of tower locations with details of types and extensions to towers, preparation of tower schedule, sag and tension calculations of conductors, preparation and supply of one copy of the approved sag templete on transparent acrylic plastic sheet after completion of all the stub setting works, two paper print copies and one tracing cloth copy of the approved profile drawing and route map with the final tower locations marked, complete in all respects as per scope & technical specifications. | km | 0 |  |  | 0 | 0
13 | Transport of dismantled materials such as tower , extensions, conductor, earthwire, insulators, hardware etc. Including loading and unloading charges | MT | 2075 | 468 | 196 | 664 | 2739
14 | Arranging scaffolding on either sides of the Main road as per the directions of KSEBL officers complete in all respects as per scope & technical specifications. | Loc | 46 | 20 | 10 | 30 | 76
15 | Labour Charges for Fixing ariel marker balls for very long spans including transportation charges etc complete as directed by deprtments/officers. Complete in all respects as per scope & specification of work & technical specifications. | Each | 50 | 0 | 0 | 0 | 50
16 | Labour Charges for providing Aviation Warning lights at top of specified towers including fixing all accessories such as solar panels, batteries and transportation charges etc. Complete as directed by deprtments/officers. Complete in all respects as per scope & specification of work & technical specifications.+ AMC for period of 5 years | Each | 20 | 0 | 0 | 0 | 20
17 | Painting towers with synthetic enamel paint of approved brand and manufacture on new tower (as per IS 5613) to give an even shade two or more coats complete in all respects as per scope & technical specifications. | sqm | 100 | 50 | 20 | 70 | 170
18 | Design, Proto Fabrication, Assembly and Type Testing (non-destructive type) of new 400KV Multi Circuit / Double Circuit towers. Complete in all respects as per scope & specification of work & technical specifications. | Each | 0 | 0 | 0 | 0 | 0
| Charges for preparation of fabrication drawings of newly designed 220kV MCMV towers as per approved design drawings | Each
| Charges for fabrication of Prototype Black towers of type including all materials as per design drawings after deducting the cost of dismantled scrap materials after type testing | MT
| Charges for proto tower transportation, assembly, supervision and co-ordination of type testing at accredited lab with 9m extension excluding the cost of type testing and dismantling after the testing | MT
| Type testing charges at accredited Lab for each type of Tower | MT
19 | Installation rate of Emergency Restoration System (ERS) Work in existing 220 KV Double circuit Line Route (ERS Equipment will be supplied by KSEB) complete in all respects as per scope & technical specifications. | Km
20 | Soil test, wherever found neccessary for asertaining type of foundation including taking pits/bore holes, collecting soil samples and testing at approved laboratories as per relevant IS codes, including cost of testing, all labour and transportion charges etc. as directed by KSEB Officers complete in all respects as per scope & technical specifications of following types:
20.1 | Soil test in all kinds of soil except rock | metre | 300 | 200 | 100 | 300 | 600
20.2 | Soil test in ordinary rock | metre | 150 | 100 | 100 | 200 | 350
20.3 | Soil test in hard rock | metre | 50 | 100 | 50 | 150 | 200
21 | Earth Work in Excavation by mechanical means (Hydraulic excavator) / manual means in foundation trenches or drains (not exceeding 1.5m in width or 10 sqm on plan), including dressing of sides and ramming of bottoms, lift upto 1.5 m, including disposal of surplus excavated soil as directed, within a lead of 50m, complete in all respects as per scope & technical specifications in:
21.1 | All kinds of soil excluding rock | cum | 0 |  | 0 | 0 | 0
21.2 | Ordinary rock | cum | 0 |  | 0 | 0 | 0
21.3 | Hard rock (requiring blasting) | cum | 0 | 0 | 0 | 0 | 0
21.4 | Hard rock (blasting prohibited) | cum | 0 |  | 0 | 0 | 0
22 | Earth Work in Excavation by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30cm in depth. 1.5 m in width as well as 10 sqm on plan) including disposal of excavated earth, lead upto 50m and lift upto 1.5m, disposed earth to be levelled and neatly dressed. complete in all respects as per scope & technical specifications in:
22.1 | All kinds of soil excluding rock | cum | 40500 | 15500 | 4600 | 20100 | 60600
22.2 | Ordinary rock | cum | 74000 | 24250 | 7000 | 31250 | 105250
22.3 | Hard rock (blasting prohibited) | cum | 450 | 525 | 275 | 800 | 1250
23 | Excavation in hard rock using non explosive agent (Chemical) or any other method without resorting to the use of conventional explosive materials etc in all lifts and conveying and depositing the excavated rock etc. at places with in a distance of 50m as directed by KSEB Engineer complete as per scope & technical specifications | cum | 450 | 450 | 0 | 450 | 900
24 | Extra for every additional lift of 1.5 m or part thereof in excavation / banking excavated or stacked materials in following soils complete in all respects as per scope & technical specifications
24.1 | All kinds of soil excluding rock | cum | 32000 | 11000 | 3200 | 14200 | 46200
24.2 | Ordinary or hard rock. | cum | 55000 | 17000 | 5250 | 22250 | 77250
25 | Close timbering in trenches including strutting, shoring and packing cavities (wherever required) complete. (Measurements to be taken of the face area timbered) complete in all respects as per scope & technical specifications:
25.1 | Depth not exceeding 1.5 m. | sqm | 11000 | 3250 | 450 | 3700 | 14700
25.2 | Depth exceeding 1.5 m but not exceeding 3 m. | sqm | 11000 | 3250 | 450 | 3700 | 14700
25.3 | Depth exceeding 3 m but not exceeding 4.5 m. | sqm | 3500 | 1200 | 200 | 1400 | 4900
26 | Open timbering in trenches including strutting and shoring complete (measurements to be taken of the face area timbered). Complete in all respects as per scope & specification of work & technical specifications.
26.1 | Depth not exceeding 1.5 m. | sqm | 2000 | 750 | 200 | 950 | 2950
26.2 | Depth exceeding 1.5 m but not exceeding 3 m | sqm | 2000 | 750 | 200 | 950 | 2950
26.3 | Depth exceeding 3 m but not exceeding 4.5 m. | sqm | 650 | 200 | 100 | 300 | 950
27 | Pumping out water caused by springs, tidal or river seepage, broken water mains or drains and the like. Complete in all respects as per scope & specification of work & technical specifications. | kilo litre | 93000 | 32000 | 3000 | 35000 | 128000
28 | Extra for Earth work in excavation in soil (Under water) by mechanical means (Hydraulic excavator) / manual means over areas (exceeding 30cm in depth, 1.5 m in width as well as 10 sqm on plan) including disposal of excavated earth, lead upto 50m and lift upto 1.5m, disposed earth to be levelled and neatly dressed, in or under water and/or liquid mud, including pumping out water as required, complete in all respects as per scope & technical specifications:
28.1 | Normal kinds of soil | cum | 0 | 0 | 0 | 0 | 0
28.2 | Ordinary rock | cum | 0 | 0 | 0 | 0 | 0
28.3 | Hard rock | cum | 0 | 0 | 0 | 0 | 0
29 | Extra for every additional lift of 1.5 m or part thereof in excavation / banking excavated or stacked materials in all kinds of soil executed in or under water and/or liquid mud, including pumping out water as required complete in all respects as per scope & technical specifications.
29.1 | Normal kinds of soil | cum | 0 | 0 | 0 | 0 | 0
29.2 | Ordinary or Hard rock | cum | 0 | 0 | 0 | 0 | 0
30 | Providing and laying in position reinforced cement concrete of specified grade excluding the cost of centering ,shuttering, finishing and reinforcement up to plinth level complete in all respects as per scope & specification of work & technical specifications.
30.1 | 1:1.5:3 (1 cement : 1.5 coarse sand : 3 graded stone aggregate 20 mm nominal size) (M20) | cum |  |  |  | 0 | 0
31 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering up to plinth level complete in all respects as per scope & specification of work & technical specifications.
31.1 | 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) (M10) | cum | 3500 | 1100 | 350 | 1450 | 4950
31.2 | 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40 mm nominal size) (M10) | cum | 0 | 0 | 0 | 0 | 0
31.3 | 1:1.5:3 (1 cement : 1.5 coarse sand : 3 graded stone aggregate 20 mm nominal size) (M20) | cum | 17500 | 6000 | 2000 | 8000 | 25500
31.4 | 1:2:4 (1 cement : 2coarse sand : 4 graded stone aggregate 40 mm nominal size) | cum | 300 | 0 | 0 | 0 | 300
31.5 | 1:2¼:3¾ (1 Cement : 2¼ coarse sand : 3¾ graded stone aggregate 20mm nominal size) , excluding the cost of centering and shuttering - All work up to plinth level | cum | 70 | 0 | 0 | 0 | 70
31.6 | Extra for laying concrete in or under water and/or liquid mud including pumping or bailing out water and removing slush etc. | cum | 0 | 0 | 0 | 0 | 0
32 | Providing and laying in position machine batched and machine mixed design mix M-50 grade cement concrete for reinforced cement concrete work, using cement content as per approved design mix, including pumping of concrete to site of laying but excluding the cost of centering, shuttering, finishing and reinforcement, including admixtures in recommended proportions as per IS: 9103 to accelerate, retard setting of concrete, improve workability without impairing strength and durability as per direction of Engineer-in-charge. All works upto plinth level | cum | 0 | 100 | 0 | 100 | 100
33 | Providing and laying in position ready mixed M-30 grade concrete for reinforced cement concrete work, using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads, having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work, including pumping of R.M.C. from transit mixer to site of laying, excluding the cost of centering, shuttering finishing and reinforcement, including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete, improve workability without impairing strength and durability as per direction of the Engineer - in - charge. All works upto plinth level | cum | 120 | 0 | 0 | 0 | 120
34 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete above plinth level with Thermo-Mechanically Treated bars complete in all respects as per scope & technical specifications. | kg | 2000000 | 420000 | 106000 | 526000 | 2526000
35 | Centering and shuttering including strutting, propping etc. and removal following complete in all respects as per scope & technical specifications:
35.1 | For foundations, footings, bases for columns | sqm | 28000 | 12000 | 3500 | 15500 | 43500
35.2 | For columns, piers, abutments, pillars, posts and struts | sqm | 8000 | 3000 | 1000 | 4000 | 12000
36 | Random rubble masonary with hard stone including levelling up with cement concrete 1:6:12 (1 cement : 6 coarse sand : 12 graded stone aggregate 20 mm nominal size) upto plinth level with cement mortar 1:6 (1 cement:6 coarse sand)complete in all respects as per scope & technical specifications:
36.1 | In foundation and plinth | cum | 2000 | 1250 | 550 | 1800 | 3800
36.2 | In superstructure above plinth level and upto floor five level | cum | 7000 | 4250 | 2000 | 6250 | 13250
36.3 | 12 mm cement plaster of mix 1:4 (1 cement: 4 fine sand) | sqm | 600 | 350 | 350 | 700 | 1300
36.4 | Flush/ Ruled pointing on stone work with cement mortar 1:3 (1 cement : 3 fine sand) | sqm | 6000 | 3250 | 1750 | 5000 | 11000
37 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift up to 1.5 m complete in all respects as per scope & technical specifications. | cum | 100600 | 35000 | 9100 | 44100 | 144700
38 | Supplying and Filling good quality earth brought from out side in the revetment and pits of towers in layers for consolidation including stacking for measurements watering, ramming, etc, complete as directed complete in all respects as per scope & technical specifications. | cum | 5000 | 3000 | 450 | 3450 | 8450
39 | Demolishing stone rubble masonry In cement mortar manually/by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of KSEB engineer complete in all respects as per scope & technical specifications. | cum | 600 | 342 | 180 | 522 | 1122
40 | Demolishing R.C.C. work manually/ by mechanical means including stacking of steel bars and disposal of unserviceable material within 50 metres lead as per direction of KSEB | cum | 0 | 0 | 0 | 0 | 0
41 | Construction of earthen ring bunds for bailing out water for excavation and stub setting with coconut cadjan and bamboos etc complete in all respects as per scope & technical specifications (provisional qty)
41.1 | Bunds up to 0.5m height, 1m bottom width and 0.5m top width | Rm | 2160 | 432 | 96 | 528 | 2688
41.2 | Bunds beyond 0.5m height,to 1m height,1.5m bottom width and 0.5m top width. | Rm | 1104 | 624 | 96 | 720 | 1824
42 | Boring, providing and installation
42.1 | Bored cast-in-situ reinforced cement concrete piles of grade M-25 of specified diameter and length below pile cap, to carry a safe working load not less than specified, excluding the cost of steel reinforcement but including the cost of boring with bentonite solution and temporary casing of appropriate length for setting out and removal of same and the length of the pile to be embedded in the pile cap etc. by Crawler mounted, telescopic boom hydraulic pilling Rig all complete, including removal of excavated earth with all its lifts and leads (length of pile for payment shall be measured up to bottom of pile cap). Note: Truck Mounted rotary/TMR/Tubewell boring machine shall not be used. -750 mm dia piles. | m | 2500 | 0 | 0 | 0 | 2500
42.2 | Bored cast-in-situ reinforced cement concrete piles of grade M-25 of specified diameter and length below pile cap, to carry a safe working load not less than specified, excluding the cost of steel reinforcement but including the cost of boring with bentonite solution and temporary casing of appropriate length for setting out and removal of same and the length of the pile to be embedded in the pile cap etc. by Crawler mounted, telescopic boom hydraulic pilling Rig all complete, including removal of excavated earth with all its lifts and leads (length of pile for payment shall be measured up to bottom of pile cap). Note: Truck Mounted rotary/TMR/Tubewell boring machine shall not be used. -1000 mm dia piles. | m | 325 | 0 | 0 | 0 | 325
42.3 | Cast in situ single under reamed piles of 500 mm diameter and length below pile cap in M-50 cement concrete, to carry a safe working load not less than specified, excluding the cost of steel reinforcement but including the cost of boring with bentonite solution and the length of the pile to be embedded in pile cap etc. all complete. (Length of pile for payment shall be measured upto to the bottom of pile cap) | m | 0 | 275 | 0 | 275 | 275
43 | Providing and laying in position machine batched and machine mixed design mix M-25 grade cement concrete for reinforced cement concrete work, using cement content as per approved design mix, including pumping of concrete to site of laying but excluding the cost of centering, shuttering, finishing and reinforcement, including admixtures inrecommended proportions as per IS: 9103 to accelerate, retard setting of concrete, improve workability without impairing strength and durability as per direction of Engineer-in-charge. (Note :- Cement content considered in this item is @ 330 kg/cum. Excess/less cement used as per design mix is payable/recoverable separately) complete in all respects as per scope & technical specifications. | cum | 0 | 0 | 0 | 0 | 0
44 | Hire charges for providing floating platform (Pontoon in steel work) 2 Nos. x 12.00 x 5.55x1.75 meter size one for providing machineries and the other for handling materials for form work etc, fabricating and hoisting in position with MS plate 6mm thick for bottom and sides, 10mm for top and stiffening both ways with 65mm x 65mm x 6mm Ms angle at 50cm c/c supporting over by ISMB - 150 200mm & 3 Nos., 6m long MS pipe is used for supporting the pontoon. 1 meter dia circular barrels having length 6.40 meter and 5.00 meter each is used on either side and 3.75 meter long is used in front side. Necessary charges are included for sot and hire charges of anchorages, pontoon, mobilization charges including painting with iron primer etc. complete for piling works in river/lake as per the directions of the departmental officers at site. Complete in all respects as per scope & technical specifications. | /metre of pile length | 0 | 0 | 0 | 0 | 0
45 | Driving down coconut piles 200 mm to 300 mm dia to approved line and levels through various strata including cost of piles, all hire and labour for fixing staging platform and all other appliances necessary for pile driving after pointing the bottom and upto 8 m depth below ground level, etc complete.in all respects as per scope & technical specifications. | RM | 10000 | 0 | 0 | 0 | 10000
46 | Fabricating, casing pipe of specified diameter with 6mm thick MS plate used for cast in situ pile including cost and conveyance of all materials, all related charges for fixing anchorages etc with all leads and lifts etc. complete for piles in river/lake according to the specification and as directed by the departmental officers complete in all respects as per scope & technical specifications. | Kg | 0 | 0 | 0 | 0 | 0
47 | Conveying pre fabricated, casing pipe of specified diameter with 6mm thick MS plate used for cast in situ pile and errecting at site in lines and levels and driven down into a required depth including cost and conveyance of all materials, all related charges for anchoring etc with all leads and lifts etc.complete for piles in river/lake as directed by the departmental officers, complete in all respects as per scope & technical specifications. | metre | 0 | 0 | 0 | 0 | 0
48 | Bored cast-in-situ specified grade R.C.C. Pile in all diametrs excluding cost of concrete and Reinforcement complete as per Drawing and Technical Specifications and removal of excavated earth with all lifts and lead upto 1000 m for all diameter of piles coming in river/lake, complete in all respects as per scope & technical specifications. | metre | 0 | 0 | 0 | 0 | 0
49 | Driving precast vertical specified grade R.C.C. Piles excluding cost of cement concrete and Reinforcement complete as per Drawing and & Technical Specification Size of pile - as specified in river/lake. Complete in all respects as per scope & specification of work & technical specifications. | metre | 0 | 0 | 0 | 0 | 0
50 | Providing and laying in position ready mixed M-35 grade concrete forreinforced cement concrete work, using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads, having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work, including pumping of R.M.C. from transit mixer to site of laying , excluding the cost of centering, shuttering finishing and reinforcement, including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete,improve workability without impairing strength and durability as per direction of KSEB for Piles and pile cap, complete in all respects as per scope & technical specifications. | cum | 0 | 0 | 0 | 0 | 0
51 | Add for using extra cement in the items of design mix over and above the specified cement content therein. | quintal | 0 | 0 | 0 | 0 | 0
52 | Boring with hydraulic piling rigs with power units, and installing cast in situ single under reamed piles of specified diameter and length below pile cap in cement concrete, to carry a safe working load not less than specified, excluding the cost of steel reinforcement and concrete but including the cost of boring with bentonite solution and the length of the pile to be embedded in pile cap etc. (Length of pile for payment shall be measured upto to the bottom of pile cap) complete in all respects as per scope & technical specifications: | m | 0 | 0 | 0 | 0 | 0
53 | Extra for providing additional bulb in under reamed piles. | each | 0 | 0 | 0 | 0 | 0
54 | Vertical load testing of piles in accordance with IS 2911 (Part IV) including installation of loading platform by Kentledge/Anchor piles method and preparation of pile head or construction of test cap and dismantling of test cap after test etc. complete as per specification & the direction of Engineer in-charge for Single pile of various tone capacities. Initial test (Test Load 2.5 times the Safe capacity) Note: 1. Initial and Routine Load Test shall not be carried out by Dynamic method of testing. Note: 2. Testing agency shall submit the design of loading platform for KSEB approval complete in all respects as per scope & technical specifications:
54.1 | Single pile upto 50 MT Safe capacity | per test | 0 | 0 | 0 | 0 | 0
54.2 | Single pile above 50 MT and upto 100 MT Safe capacity | per test | 0 | 0 | 0 | 0 | 0
54.3 | Single pile upto 50 tonne Safe capacity, Routine test (Test Load 1.5 times the Safe capacity) | per test | 0 | 0 | 0 | 0 | 0
54.4 | Single pile above 50 tonne and upto 100 tonne Safe capacity, Routine test (Test Load 1.5 times the Safe capacity) | per test | 0 | 0 | 0 | 0 | 0
55 | Boring holes of dia 32 to 100mm or nearest size dia on hard rock where anchoring is found necessary to accommodate anchor bars/stubs including hire charges of machinery, T&P, pilot vehicle to carry other materials, grouting charges etc. Complete in all respects as per scope & technical specifications | m | 550 | 550 | 300 | 850 | 1400
56 | Providing and laying in position ready mixed M-25 grade concrete forreinforced cement concrete work, using cement content as per approved design mix, manufactured in fully automatic batching plant and transported to site of work in transit mixer for all leads, having continuous agitated mixer, manufactured as per mix design of specified grade for reinforced cement concrete work, including pumping of R.M.C. from transit mixer to site of laying , excluding the cost of centering, shuttering finishing and reinforcement, including cost of admixtures in recommended proportions as per IS : 9103 to accelerate/ retard setting of concrete,improve workability without impairing strength and durability as per direction of the Engineer-in-charge as per the scope and technical specifications | M3 | 0 | 0 | 0 | 0 | 0
57 | Tension stringing using Tension Puller Machine as per standard of following conductors including attaching insulator strings with arcing horns or rings on to the tower cross arms, clamping the conductor to the insulator strings using suspension clamps with armour rods and tension clamps, jumpering the conductors at tension points, jointing the conductors and pilot wire wherever necessary, installation of vibration dampers, hire charges of tractor and stringing tools, all hire and labour for protective trestle work, providing suitable back stays at the time of stringing, etc. Complete in all respects as per scope & technical specifications
57.1 | 6 Line ACSR Kundah | km |  | 0 | 0 | 0 | 0
57.2 | 6 Line ACSR Panther | km |  | 0 | 0 | 0 | 0
58 | Paving out, stringing and tensioning as per standard of 3 line ACSR WOLF' conductors including attaching insulator strings with arcing horns or rings on to the tower cross arms, clamping the conductor to the insulator strings using suspension clamps with armour rods and tension clamps, jumpering the conductors at tension points, jointing the conductors and pilot wire wherever necessary, installation of vibration dampers, hire charges of tractor and stringing tools, all hire and labour for protective trestle work, providing suitable back stays at the time of stringing, etc. complete in all respects as per scope & technical specifications | km | 0 | 0.38 | 0 | 0.38 | 0.38
59 | Finishing with Epoxy paint (two or more coats) at all locations prepared and applied as per manufacturers specifications including appropriate priming coat, preparation of surface etc complete in all respects as per scope & technical specifications | Sqm | 17000 | 0 | 0 | 0 | 17000
60 | Clearing jungle including uprooting of rank vegitation, grass,brush wood,trees and saplings of girth upto 30cm measured at a height of 1m above ground level and removal of rubbish upto a distance of 50m outside the periphery of the area cleared complete in all respects as per scope & technical specifications | Sqm |  |  |  | 0 | 0
61 | Erection,Testing and Commissioining of Joint Box (48 Fibre) | Nos. |  |  |  | 0 | 0
62 | Erection,Testing and Commissioining of FODP 48 fibre for 48 Fibre OPGW - ASLH-D(S)b 48 SMF (A20SA 79-6.4) | Nos. |  |  |  | 0 | 0
63 | Erection of name boards, phase indicator, number plates, danger boards,circuit plates etc. as per standards on all towers | LS |  |  |  | 0 | 0

## BOQ-Material and spares
Construction/Up-gradation of 220/110kV MCMV line
| Name of work: |  | Name of Packages:
| KLSP Project A& KLSP Project B |  | Kolathunadu Line strengthening Package- Up-grading 110kV SC line to 220/110kV MCMV line from Kanhirode to Mylatty line on Turnkey Basis (KLSP Project A and KLSP Project B)
| NMLP-A |  | Malabar Lines Package- PHASE 1A: Up-grading of 110kV SC & 66kV SC line from Mundayad to Thalassery to 220/110kV MCMV line on Turnkey Basis (NMLP Project A)
| NMLP-B |  | North Malabar Lines Package Phase 1B:- Construction/Upgradation of 220/110 KV MCMV line from Areekode- Kaniyambetta LILO point (near Malayamma) to Kunnamangalam S/S through Agasthiyamuzhi 110 kV DC line route on Turnkey Basis (NMLP Project B)
SL. NO. | ITEM DESCRIPTION | BILL OF QUANTITIES - MATERIAL
|  | UNIT | Kolathunadu Package |  | North Malabar | [5 empty] | Total Qty - KLSP+NMLP
|  |  | (KLSP Project A and KLSP Project B) | Spares | Project A | Project B | Total Qty | Spare A | Spare B | Spare Total Qty | Total Qty - Main | Total Qty - Spares
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8=6+7 | 9 | 10 | 11=9+10 | 12=4+8 | 13=5+11
1 | Towers & Tower accessories
1.1 | Manufacturing, Testing and Supply of 400/220kV& 220/110kV MultiCircuit Multi Voltage, 220/220kV &110/110kV MC Lattice Type Hot Dip Galvanized Steel Towers and Stub & cleat of various types (MLD for 400/220kV, KLA/B/C/D for 220/110kV, MD for 220/220kV & M3,M60 for 110/110kV ) complete with all tower parts & Extensions, Templates, including fastners, bolts & nuts,anti theft bolts and nuts along with spring washers , step bolts, hangers, D-shackles, pack washers, Danger plate, Circuit Plates,Number plate, Phase plate, Anti Climbing Device, Bird Guard, etc.complete in all respect as per scope & Technical specifications | MT | 6100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6100 | 0
1.2 | Manufacturing, Testing and Supply of 400/220kV& 220/110kV Multi Circuit Multi Voltage & 220/220kV MC Lattice Type Hot Dip Galvanized Steel Towers and Stub & cleat of various types (MLD& MLS for 400/220kV, KLA/B/C/D for 220/110kV, MA & MB for 220/220kV ) complete with all tower parts & Extensions, Templates, including fastners, bolts & nuts,anti theft bolts and nuts along with spring washers , step bolts, hangers, D-shackles, pack washers, Danger plate, Circuit Plates, Number plate, Phase plate, Anti climbing device, Bird Guard, etc.complete in all respect as per scope & Technical specifications | MT | 0 | 0 | 2222 | 0 | 2222 | 0 | 0 | 0 | 2222 | 0
1.3 | Manufacturing, Testing and Supply of 220/110kV MultiCircuit Multi Voltage, Lattice Type Hot Dip Galvanized Steel Towers and Stub & cleat of various types ( KLA/B/C/D ) complete with all tower parts & Extensions, Templates, including fastners, bolts & nuts,anti theft bolts and nuts along with spring washers , step bolts, hangers, D-shackles, pack washers, Danger plate,Circuit Plates, Number plate, Phase plate, Anti climbing device, Bird Guard, etc.complete in all respect as per scope & Technical specifications | MT | 0 | 0 | 0 | 736 | 736 | 0 | 0 | 0 | 736 | 0
1.4 | Manufacturing,Testing and Supply of Pipe Type Earthing set with 25NB Hot Dip GI Pipe (3000mm long), Set of flat 50x6 (5000mm long) with bolts, nuts & spring washers complete in all respect as per scope & Technical specifications | No | 584 | 0 | 196 | 58 | 254 | 0 | 0 | 0 | 838 | 0
1.5 | Manufacturing,Testing and Supply of Counter poise Earthing set with following accessories Hot Dip Galvanized Steel Wire 7/3.0mm (120 m long), Legs for Counterpoise compression joints, Any other required groove clamps, connectors etc. complete in all respect as per scope & Technical specifications | No | 20 | 0 | 20 | 3 | 23 | 0 | 0 | 0 | 43 | 0
2 | Conductors and Conductor Accessories
2.1 | Manufacturing, Testing & Supply of following type of Conductors complete in all respect as per scope & technical specifications:
2.1.1 | ACSR 30/3mm Al 7/3mm steel Panther Conductor | km | 1540 | 0 | 324 | 142 | 466 |  |  | 0 | 2006 | 0
2.1.2 | ACSR Kundah - Conductor | km | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0
| ACSR 54/3.18mm Al 7/3.18mm steel Zebra | km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACSR 54/3.53mm Al 7/3.53mm steel Moose | km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACSR 30/2.59mm Al 7/2.59mm steel Wolf | km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACCC Drake equivalent conductor | km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.2 | Manufacturing, Testing & Supply of Midspan Compression joint for following type of conductor complete in all respect as per Scope and technical specification
2.2.1 | ACSR Panther Conductor | No | 847 | 9 | 178 | 78 | 256 | 18 | 8 | 26 | 1103 | 35
2.2.2 | ACSR Kundah Conductor | No | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0
| ACSR Zebra Conductor | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACSR Moose Conductor | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACSR 30/2.59mm Al 7/2.59mm steel Wolf | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACCC Drake equivalent conductor | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.3 | Manufacturing, Testing & Supply of Repair Sleeve for following type of conductor complete in all respect as per Scope and technical specification
2.3.1 | ACSR Panther Conductor | No | 254 | 3 | 54 | 23 | 77 | 5 | 2 | 7 | 331 | 10
2.3.2 | ACSR Kundah Conductor | No | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0
| ACSR Zebra Conductor | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACSR Moose Conductor | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACSR 30/2.59mm Al 7/2.59mm steel Wolf | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACCC Drake equivalent conductor | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.4 | Manufacturing, Testing & Supply of T-Connector for following type of conductor complete in all respect as per Scope and technical specification
2.4.1 | ACSR Panther Conductor | No | 54 | 1 | 30 | 48 | 78 | 3 | 5 | 8 | 132 | 9
2.4.2 | ACSR Kundah Conductor | No | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0
| ACSR Zebra Conductor | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACSR Moose Conductor | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACSR Wolf conductor | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACCC Drake equivalent conductor | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.5 | Manufacturing, Testing & Supply of Vibration Dampers for following type of conductor complete in all respect as per Scope and technical specification
2.5.1 | ACSR Panther Conductor | No | 6110 | 0 | 666 | 351 | 1017 | 33 | 18 | 51 | 7127 | 51
2.5.2 | ACSR Kundah Conductor | No | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 0
| ACSR Zebra Conductor | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACSR Moose Conductor | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACSR Wolf conductor | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACCC Drake equivalent conductor | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.6 | Manufacturing, Testing & Supply of Single Tension Hardware Fittings for following type of conductor complete in all respect as per Scope and technical specification
2.6.1 | 110kV ACSR Panther Conductor | No | 2460 | 25 | 297 | 327 | 624 | 15 | 33 | 48 | 3084 | 73
2.6.2 | 220kV ACSR Kundah Conductor | No | 144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144 | 0
| ACSR Zebra Conductor | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACSR Wolf conductor | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACCC Drake equivalent conductor | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.7 | Manufacturing, Testing & Supply of Single Suspension Hardware Fittings for following type of conductor complete in all respect as per Scope and technical specification
2.7.1 | 110kV ACSR Panther Conductor | No | 450 | 5 | 42 | 6 | 48 | 4 | 1 | 5 | 498 | 10
2.7.2 | 110kV ACSR Panther Conductor (Pilot suspension) | No | 660 | 13 | 72 | 85 |  | 7 | 9 |  | 660 | 13
2.7.3 | 220kV ACSR Kundah Conductor | No | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0
2.7.3 | 220kV ACSR Kundah Conductor (Pilot suspension) | No | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0
| ACSR Zebra Conductor | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Quad Bundle ACSR Moose Conductor (For 400 KV Pilot String) | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACSR Wolf conductor | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.8 | Manufacturing, Testing & Supply of Double Suspension Hardware Fittings for following type of conductor complete in all respect as per Scope and technical specification
2.8.1 | 110kV ACSR Panther Conductor | No | 72 | 1 | 12 | 12 | 24 | 1 | 1 | 2 | 96 | 3
| 220kV ACSR Kundah Conductor | No | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| ACSR Zebra Conductor | No | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| ACSR Wolf conductor | No | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
2.9 | Manufacturing, Testing & Supply of Double Tension Hardware Fittings for following type of conductor complete in all respect as per Scope and technical specification
2.9.1 | 110kV ACSR Panther Conductor | No | 170 | 2 | 48 | 24 | 72 | 5 | 2 | 7 | 242 | 9
| 220kV ACSR Kundah Conductor | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACSR Zebra Conductor | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Quad Bundle ACSR Moose Conductor (For 400 KV Pilot String) | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACSR Wolf conductor | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ACCC Drake equivalent conductor | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.10 | Manufacturing, Testing & Supply of Preformed Armour Rod for following type of conductor complete in all respect as per Scope and technical specification
2.10.1 | ACSR Panther Conductor | No | 3480 | 35 | 823 | 273 | 1096 | 41 | 27 | 68 | 4576 | 103
2.10.2 | ACSR Kundah Conductor | No | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0
2.10.3 | ACSR Zebra Conductor | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.11 | Manufacturing, Testing & Supply of Hardware set for ACSR Panther Conductor complete in all respect as per Scope and technical specification
2.11.1 | 220kV Twin Bundle tension Hardware set | No | 2630 | 26 | 945 | 339 | 1284 | 47 | 34 | 81 | 3914 | 107
2.11.2 | 220kV Twin Bundle Pilot Suspension Hardware set | No | 660 | 7 | 233 | 85 | 318 | 23 | 9 | 32 | 978 | 39
2.11.3 | 220kV Twin Bundle V String Suspension Hardware | No | 450 | 5 | 115 | 6 | 121 | 12 | 1 | 13 | 571 | 18
2.12 | Manufacturing, Testing & Supply of Hardware set for Twin ACSR Panther Conductor complete in all respect as per Scope and technical specification
| 220 KV Twin Bundle V String Suspension Hardware set | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Double Tension Hardware Fittings | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Single Suspension Hardware fittings ( For 220 KV Pilot String ) | No |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| V String Suspension Hardware set for ACCC Drake equivalent conductor including conductor accessories | Set | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Single Pilot Suspension Hardware set for ACCC Drake equivalent conductor including PA rod | Set | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2.13 | Spacer Damper suitable for Twin ACSR Panther Conductor | Set | 8730 | 44 | 3454 | 870 | 4324 | 35 | 44 | 79 | 13054 | 123
2.13.1 | Rigid Spacer suitable for Twin ACSR Panther Conductor | Set | 2610 | 13 | 933 | 336 | 1269 | 47 | 17 | 64 | 3879 | 77
2.14 | Spacer Damper suitable for ACSR Quad-Moose Conductor | Set | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Polymeric Insulators
3.1 | Manufacturing, Testing and Supply of Silicone Rubber Housed Long rod composite polymer Insulator of following items complete in all respect as per scope and technical specifications
3.1.1 | 110kV, 70KN Silicon Composite Longrod Insulators | No | 1254 | 13 | 138 | 115 | 253 | 14 | 6 | 20 | 1507 | 33
3.1.2 | 110kV, 90KN Silicon Composite Longrod Insulators | No | 2800 | 28 | 393 | 375 | 768 | 39 | 19 | 58 | 3568 | 86
3.1.3 | 220kV, 90KN Silicon Composite Longrod Insulators | No | 2256 | 23 | 697 | 182 | 879 | 70 | 9 | 79 | 3135 | 102
3.1.4 | 220kV, 120KN Silicon Composite Longrod Insulators | No | 5404 | 54 | 1891 | 679 | 2570 | 95 | 34 | 129 | 7974 | 183
| 400kV, 120KN Silicon Composite Longrod Insulators | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 400kV, 160KN Silicon Composite Longrod Insulators | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[11 empty] | 0 | 0
4 | OPGW & Accessories | [9 empty] | 0 | 0
4.1 | Manufacturing, Testing & Supply 48 Fiber ASLH-D(S)b48SMF (A20 SA 79 6.4) DWSM OPGW Cable | km | 90 | 1 | 23 | 8 | 31 |  | 1 | 1 | 121 | 2
4.2 | Supply of Hardware set for 48 fibre OPGW OFC including cable fittings and all accessories (per Km Rate) | km |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
4.3 | Manufacturing, Testing & Supply of following OPGW Accessories complete in all respect as per scope and technical specifications
4.3.1 | Joint Box (48 Fibre) | No | 30 | 0 | 7 | 4 | 11 | 1 | 0 | 1 | 41 | 1
4.3.2 | FODP 48 fibre for 48 Fibre OPGW - ASLH-D(S)b 48 SMF (A20SA 79-6.4) | No | 4 | 0 | 7 | 2 | 9 | 1 | 0 | 1 | 13 | 1
4.3.3 | Suspension Assembly for 48 Fibre OPGW - ASLH-D(S)b 48 SMF (A20SA 79-6.4) | No | 75 | 1 | 19 | 2 | 21 | 2 | 0 | 2 | 96 | 3
4.3.4 | Tension Assembly for 48 Fibre OPGW - ASLH-D(S)b 48 SMF (A20SA 79-6.4) | No | 157 | 2 | 141 | 48 | 189 | 14 | 5 | 19 | 346 | 21
4.3.5 | Dead end Assembly for 48 Fibre OPGW - ASLH-D(S)b 48 SMF (A20SA 79-6.4) | No | 60 | 1 | 14 | 2 | 16 | 1 | 0 | 1 | 76 | 2
4.3.6 | Tension Assembly (For Joint Box Locations) for 48 Fibre OPGW - ASLH-D(S)b 48 SMF (A20SA 79-6.4) | No | 60 | 1 | 14 | 8 | 22 | 1 | 1 | 2 | 82 | 3
4.3.7 | Pass through Assembly for 48 Fibre OPGW - ASLH-D(S)b 48 SMF (A20SA 79-6.4) | No | 75 | 1 | 78 | 28 | 106 | 8 | 3 | 11 | 181 | 12
4.3.8 | Tension Assembly at Susp. Tower (For Joint Box Locations) for 48 Fibre OPGW - ASLH-D(S)b 48 SMF (A20SA 79-6.4) | No | 10 | 0 | 4 | 1 | 5 |  | 0 | 0 | 15 | 0
4.3.9 | Vibration Damper for 48 Fibre OPGW - ASLH-D(S)b 48 SMF (A20SA 79-6.4) | No | 584 | 6 | 194 | 59 | 253 |  | 6 | 6 | 837 | 12
4.3.10 | Down Lead Clamp Assembly for 48 Fibre OPGW - ASLH-D(S)b 48 SMF (A20SA 79-6.4) | No | 150 | 2 | 70 | 40 | 110 | 7 | 4 | 11 | 260 | 13
4.3.11 | Flexible aluminium Bond with Y type Clamp | No | 509 | 5 | 190 | 58 | 248 | 10 | 6 | 16 | 757 | 21
4.3.12 | Fibre Optic Approach Cable- 48 Fibre | m | 1200 |  | 600 | 300 | 900 |  |  | 0 | 2100 | 0
4.3.13 | HDPE Pipe 40 mm | m | 1200 |  | 600 | 300 | 900 |  |  | 0 | 2100 | 0
4.3.14 | GI Cable Tray with clamp, B&N, suitable for Approach cable- 48 Fibre | m | 200 |  | 50 | 50 | 100 | 5 |  | 5 | 300 | 5
4.3.15 | Cable loop bracket | No | 60 | 0 | 7 | 4 | 11 | 1 | 0 | 1 | 71 | 1
5 | Earthwire & Accessories
5.1 | Manufacturing, Testing and Supply of Earthwire & Accessories complete as per scope and technical specifications
| GI Earthwire 7/9 SWG | km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Single Tension hardware set for 7/9 SWG Earthwire with copper bond | No | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Miscellaneous Accessories
6.1 | Manufacturing, Testing and Supply of Ariel Marker Balls fluroscent complete as per scope & technical specifications | No | 50 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 1
6.2 | Manufacturing, Testing and Supply of Low intensity Avation Obstruction light ( Fixed Red LED) with 90Wp solar power module and 12V, 60Ah MF battery having minimum 2 days back-up with necessary control panels and automatic Dusk to dawn controller confirming ICAO in a suitable OD weather proof cabinet for mounting on MCMV Towers | No | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0

## BOQ-Dismantled
Construction/Up-gradation of 220/110kV MCMV line
| Name of work: |  | Name of Packages:
| KLSP Project A& KLSP Project B |  | Kolathunadu Line strengthening Package- Up-grading 110kV SC line to 220/110kV MCMV line from Kanhirode to Mylatty line on Turnkey Basis (KLSP Project A and KLSP Project B)
| NMLP-A |  | Malabar Lines Package- PHASE 1A: Up-grading of 110kV SC & 66kV SC line from Mundayad to Thalassery to 220/110kV MCMV line on Turnkey Basis (NMLP Project A)
| NMLP-B |  | North Malabar Lines Package Phase 1B:- Construction/Upgradation of 220/110 KV MCMV line from Areekode- Kaniyambetta LILO point (near Malayamma) to Kunnamangalam S/S through Agasthiyamuzhi 110 kV DC line route on Turnkey Basis (NMLP Project B)
| Dismantled items | [7 empty] | KLSP Project A & Project B Package - List of Dismantled Materials |  |  |  | NMLP Project A - List of Dismantled Materials |  |  |  | NMLP Project B - List of Dismantled Materials
Sl No | Item | Kolathunadu Package QTY | North Malabar QTY |  | Total QTY | Unit | Est. Rate (INR) | Est Amount (INR) | Sl No | Item | Unit | Qty | Sl No | Item | Unit | Qty | Sl No | Item | Unit | Qty
|  | (KLSP Project A and KLSP Project B) | Project A | Project B |  |  |  |  | 1 | Dismanted Towers, extensions etc. | MT | 1650 | 1 | Dismanted Towers, extensions etc. | MT | 370 | 1 | Dismanted Towers, extensions etc. | MT | 155
1 | 2 | 3 | 4 | 5 | 6=3+4+5 | 7 | 8 | 9=8*6 | 2 | Dismantled ACSR Conductors | MT | 260 | 2 | Dismantled ACSR Conductors | MT | 60 | 2 | Dismantled AAAC Conductors | MT | 20
1 | Cost of Dismantled ACSR/AAAC conductor | 260 | 60 | 20 | 340 | MT | 84000 | 28560000 | 3 | Dismantled earth wire | MT | 60 | 3 | Dismantled earth wire | MT | 15 | 3 | Dismantled earth wire | MT | 5
2 | Cost of Dismantled Copper conductor | 0 | 0 | 0 | 0 | MT | 315000 | 0 | 4 | Disc Insulator | MT | 70 | 4 | Disc Insulator | MT | 20 | 4 | Disc Insulator | MT | 10
3 | Cost of Dismantled 7/9 or 7/10 stranded Galvanized steel earthwire | 60 | 15 | 5 | 80 | MT | 14000 | 1120000
4 | Cost of Dismantled Insulators and accessories, power conductor accessories, Earth conductor accessories etc. | 70 | 20 | 10 | 100 | MT | 5000 | 500000
5 | Cost of Dismantled Galvanized Tower parts -Scrap iron | 1650 | 370 | 155 | 2175 | MT | 14000 | 30450000
| Total Amount | [6 empty] | 60630000